3-Part CSI MasterFormat Specification

SECTION 07 7200

Roof Accessories: roof hatch and smoke vent

- Rev 07/26

- General

      - SUMMARY

        - Section includes:

          - Hatch type Heat and Smoke Vents

            - AcousticMAX Acoustical STC48 smoke vents are sound transmission class rated for stages and theaters.

            - AcousticMAX Acoustical STC50 smoke vents are sound transmission class rated in compliance with IBC 1207.

      - Related Requirements:

        - Division 05 for ladders and stairs.

        - Division 07 for roofing and sealants.

      - COORDINATION

        - Coordinate layout and installation of roof accessories with roofing membrane and base flashing and interfacing and adjoining construction to provide a watertight installation.

        - Coordinate dimensions with rough-in information or Shop Drawings of equipment to be supported.

      - Action SUBMITTALS

        - Shop Drawings: Indicate configuration and dimension of components, adjacent construction, required clearances and tolerances, and other affected Work.

          - Hatch Units: Show types, elevations, thickness of metals, and full-size profiles.

          - Hardware: Show materials, finishes, locations of fasteners, types of fasteners, locations and types of operating hardware, and details of installation.

          - General: Show connections of units and hardware to other Work. Include schedules showing location of each type and size of unit

        - Product Data: Manufacturer’s technical data for each type of hatch assembly, including setting drawings, templates, finish requirements, and details of anchorage devices.

          - Include complete schedule, types, locations, construction details, finishes, latching or locking provisions, and other pertinent data.

      - informational submittals

        - Provide manufacturer's standard warranty.

        - Sustainable Design Submittals:

          - Building Product Disclosure Requirements: To encourage the use of building products that are working to minimize their environmental and health impacts, provide the following information when available:

            - Material Ingredients Documentation demonstrating the chemical inventory of the product

      - Closeout submittals

        - Manufacturer's Installation Instructions and Operation & Maintenance:  Indicate installation, operation and maintenance requirements and rough-in dimensions.

      - Quality Assurance

        - Regulatory Requirements:

          - International Building Code (IBC) Section 1013.6 Roof Access

          - International Building Code (IBC) Section 1009.11 Means of Egress, Stairways, Stairway to Roof

          - International Building Code for venting requirements

          - IBC Section 410 for Stages and Platforms

          - IBC Section 910 for Factory and Storage occupancies

          - IBC Section 1207 Sound Transmission

          - Underwriters Laboratories Inc, UL 793 Listed for Heat and Smoke Vents

          - FM Global, Factory Mutual, FM 4430 Heat and Smoke Vents for Roofs

          - Reference NFPA 204 for general maintenance of Heat and Smoke vents.

          - ASTM E 90 Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements

      - DELIVERY, STORAGE, and HANDLINg

        - Deliver materials to Project site ready use.

        - Exercise proper care in handling of Work so as not to disrupt finished surfaces.

        - Store materials under cover in a dry and clean location off the ground.

      - WARRANTY

        - Provide manufacturer's standard 5 year warranty. Roof hatches and smoke vents shall be free from manufacturing defects in materials and fabrication for a period of 5 years from the date of shipment. Should a product fail to function in normal use within this period, manufacturer shall furnish a replacement or new part at Babcock-Davis discretion.

- PRODUCT

      - MANUFACTURER

        - Babcock-Davis

9300 73rd Ave N

Brooklyn Park, MN 55428

PH: 888.412.3726

www.BabcockDavis.com

          - Type and Size: Acoustical Smoke Vents, AcousticMAX SV, rated per ASTM E 90 and OITC rated per ASTN E 1332.

            - Performance:

              - Certification: Smoke vent to have official UL label for testing to UL 793 Smoke and Heat Vents [,and FM 4430 Approved].

              - STC Rating: [STC 50 - OITC 47, model BSVZ] [STC 50 - OITC 39, model BSVY] Rated per ASTM E 90 and OITC rated per ASTM E 1332.

              - Loads: 40-lbf/sq. ft. (1.9-kPa) live load with a maximum deflection of 1/150th of the span; 90 lbf/sq. (4.3 kPa) wind uplift.

              - When release is actuated, lid shall open against 10-lbf/sq. ft. (0.5-kPa) snow or wind load and lock in position.

            - Door Options:

              - Double Door: [48 by 48 inches (1220 by 1220 mm)] [48 by 96 inches (1220 by 2440 mm)] [60 by 60 inches (1525 by 1525 mm)] [60 by 96 inches (1525 by 2440 mm)] [60 by 120 inches (1525 by 3050 mm)] [72 by 72 inches (1830 by 1830 mm)] [72 by 96 inches (1830 by 2440 mm)] [Size as indicated on Drawings] <Insert dimensions>.

              - Quad Door: [66 by 144 inches (1675 by 3660 mm)] [72 by 120 inches (1830 by 3050 mm)] [72 by 144 inches (1830 by 3660 mm)] [Size as indicated on Drawings]

            - Hatch Material:

              - Cover: [STC 50 - OITC 47 0.1046-inch (2.65 mm)] [STC 50 - OITC 39, 0.07895-inch (1.9 mm)] galvanneal steel cover and liner.

              - Curb and Cover Insulation: STC 50 - OITC 47, 4 inch (102 mm) Mineral Wool insulation with sound mat contained within 4-1/4 inch (108 mm) thick covers, providing total thermal resistance of R-16.8][STC 50 - OITC 39, 3 inch (83 mm) Mineral Wool insulation with sound mat contained within 3-1/4 inch (108 mm) thick covers, providing total thermal resistance of R-12.6].

Curb height in "Curb" paragraph below may be determined by adding thickness of roof insulation to the minimum base flashing height recommended by roofing membrane manufacturer or established by office practice.

              - Curb: [STC 50 - OITC 47 0.1046-inch (2.65 mm)] [STC 50 - OITC 39, 0.07895-inch (1.9 mm)] galvanneal steel curb. 12 inch (305 mm) high double wall curb with EZ tab counterflashing and 5-1/2 inch (140 mm) mounting flange with 1/2 inch (13 mm) diameter holes.

            - Finish:

              - Cover Exterior: [ANSI 70 powder coat steel][High Reflectance White powder coat steel.] [As selected by Architect from manufacturer's full range] <Insert color>

              - Cover Interior: Black powder coat finish.

              - Curb: Black powder coat finish.

            - Latch: Positive hold zinc plated steel rotary latch Upon latch releases, vent covers are closed manually at rooftop level.

              - Latch released manually via internal and external pull handles with cables.

              - Latch released automatically by UL 33 listed fusible melt-out link at temperature of [165 deg F (74 deg C)] [212 deg F (100 deg C)] [280 deg F (138 deg C)] [350 deg F (177 deg C)] [360 deg F (182 deg C)] [370 deg F (188 deg C)] [386 deg F (197 deg C)] [450 deg F (232 deg C)].

            - Options and Accessories

              - Burglar Bars:  [1/2 inch (13 mm)] [3/4inch (19 mm)] diameter steel rod [6 inches (152 mm) by 12 inches (305 mm)] [6 inches (152 mm) by 6 inches (152 mm)] spacing, attached to inside of curb.

              - Fall Protection Security Mesh: 3/16 inch (4.8 mm) diameter steel rod, 4 inch (102 mm) by 4 inch (102 mm) spacing, securely attached to inside of curb.

              - Manual Winch: Operation allowing remote closing of smoke vent from the floor area.

              - Optional latch release with electrical Belimo motor actuator, [24 V DC/AC] [110 VAC].

              - Linear Actuator Operation allowing remote opening and closing of smoke vent. Push button operator includes open and close.

- EXECUTION

      - EXAMINATION

- Verification of Conditions: Examine areas and conditions under which Work is to be performed and identify conditions detrimental to proper or timely completion.

- Verify that deck, curbs, roof membrane, base flashing, and other items affecting Work of this Section are in place and positioned correctly.

- Verify tolerances and correct improper condition

- Identify conditions detrimental to providing proper quality and timely completions of work.

- Do not proceed with installation until detrimental conditions have been corrected.

      - Installation

- Comply with manufacturer's recommendations.

- Coordinate installation of components of this Section with installation of roof deck, roof structure, roofing membrane, and base flashing.

- Coordinate installation of sealant and roofing cement with Work of this Section to ensure water tightness.

- Securely anchor roof accessories in compliance with manufacturer's instructions.

- Set units plumb, level, and true to line without warp or rack. Separate metal from incompatible metal or corrosive substrates, including wood, by coating concealed surfaces, at locations of contact, with bituminous coating or providing other permanent separation.

- Flange Seals: Unless otherwise indicated, set flanges of accessory units in a thick bed of roofing cement to form a seal

      - FIELD QUALITY CONTROL

- Smoke Vent Testing: Test for proper operation after installation by one or all of the operational methods:

- Melting fusible link for inside at smoke vent level recommend using handheld propane tank torch. Replace fusible link, then close vents from the exterior at the roof top level.

- Pull internal and/or external manual pull handles and then close vents from the exterior at the roof top level.

- If applicable; open the vents using an electrical signal for fire alarm, push button or other, then close vent from the exterior at the roof top level.

- Do not paint the internal mechanisms, especially moving parts such as spring/dampers, rotary latches and especially the fusible links. Painting any of these components may damage the vents and will void the warranty.

      - ADJUSTING

        - Adjust movable parts for smooth operation

        - Operational Units:  Test-operate units with operable components. Clean and lubricate joints and hardware. Adjust for proper operation.

      - cleaning

- Clean exposed surfaces per manufacturer's written instructions. Touch up damaged metal coatings.

END OF SECTION